## Slide 1: COMPONENT IDENTIFICATION AND INSTALLATION GUIDELINES FLOODBREAK, AUTOGATE
FloodBreak, L.L.C.
2800 Post Oak Blvd., Suite 5850
Houston, Texas
77056

## Slide 2
COMPONENT IDENTIFICATION

## Slide 3: GATE:
The term “gate” refers to the buoyant composite beam itself. Identified here in red.

## Slide 4: GATE PAN:
The gate pan is a recessed pan that the gate to and fits into. Identified in green.

## Slide 5: INSTALLATION BRACKET:
The installation bracket is welded to the gate pan and is used for leveling the gate unit, as well as anchoring the gate unit to the structural footing. Identified in blue.

## Slide 6: GATE UNIT:
The entire structure, including the gate, gate pan, installation bracket, and wiper walls (not shown here).

## Slide 7: INSTALLATION PLEASE NOTE THAT THE PHOTOS USED IN THIS PRESENTATION MAY REFLECT VARYING SITE CONDITIONS AND ARE INTENDED FOR ILLUSTRATION PURPOSES ONLY

## Slide 8
Installation Kit
5/8” AND 9/16”
MASONRY BITS
LEVELING
BOLTS
GATE ANCHOR BOLTS
WASHERS AND NUTS
VINYLESTER
CAPSULES
PAINT, FILLER PUTTY AND HARDENER
WIPER WALL
ANCHOR BOLTS
GRATING LIFTING HANDLES
STAINLESS SHACKLES AND LIFTING CABLE

## Slide 9: Identify the size of the of the rough opening required to accommodate placement of the gate unit.
EXAMPLE: Proposed gate size 3‘X 25’
The additions to the gate dimension are constant regardless of the gate size.
For a 3’ gate the equation to identify the rough opening (r.o.) would read as follows.
3’ (gate) + 1’-3” (gate pan) + 1’ (installation bracket) + 2’ (construction tolerance) = 7’-3” r.o.
EXAMPLE: Proposed gate size 5’-6” X 25’
For a 3’-6” gate the equation to identify the rough opening (r.o.) would read as follows.
5’-6”(gate) + 1’-3” (gate pan) + 1” (installation bracket) + 2’ (construction tolerance) = 9’-9” r.o.
THE ROUGH OPENING DEPTH IS THE “UNIT DEPTH” + 3”
STANDARD = 12”
ROADWAY = 16”
STEP 1

## Slide 10: Make two parallel saw cuts the correct distance apart as is determined by the rough opening dimension
STEP 2

## Slide 11: Break out, and haul off site the existing concrete.
STEP 3

## Slide 12: Excavate, and haul off site, the existing base to the required depth to accommodate the structural footing
STEP 4

## Slide 13: STRUCTURAL FOOTING
The structural footing is a concrete footing placed 16” below finished grade to a depth determined by others. Varying geotechnical conditions and temperatures typically determine the required depth. Consultation with an engineer or local contractor is highly recommended. Load specifications are to be equal to or greater than the existing or proposed driveway design.

## Slide 14
Place the 4” drain to storm sewer or exit point, centered both directions in the rough opening, leaving the “stub up “ high (above finished grade) to be cut off at the time of placing the gate unit.
STEP 5

## Slide 15
Place re-bar and concrete for structural footing (first lift)
STEP 6

## Slide 16
STEP 7
Remove all crating material from the gate unit. Including the wiper wall support angles and square tubing shims.

## Slide 17
STEP 8
Using a spreader-bar of adequate length to make a two point lift, lift the gate unit from the trailer and swing it into position over the rough opening.

## Slide 18
Spreader Bar

## Slide 21
STEP 9
Leaving the gate unit suspended over the rough opening, screw the leveling bolts (provided) into the installation bracket approximately 1 ½” – 2”. When the gate unit is placed it should be very close to finished grade.
Leveling Bolt

## Slide 23
STEP 10
Cut off the 4” drain to allow the leveling bolts to sit firmly on the structural footing when the gate is placed. NOTE: Using a site level, make a mark on the 4” pipe at finished grade. Measure down from finished grade 4 ½” and cut off the pipe. This will leave some pipe in the pan to be finished later.

## Slide 26
STEP 11
Place the gate unit in the rough opening making sure to keep the gate unit square with the existing structure before anchoring

## Slide 27
STEP 12
Level the gate unit to match existing grade. NOTE: Using a site level, shoot several points on the existing concrete (both sides) to determine an “average” finished grade. Placing the mast on the finish angles of the gate unit, take shot at every leveling bolt location and use the leveling bolts to bring the gate unit to “average” finished grade.

## Slide 29: STEP 13 Anchor the gate unit to the structural footing.
Using a rotor hammer and a 9/16” masonry bit (provided) drill a minimum of 6” into the structural footing by placing the into the anchor holes located adjacent to the leveling bolts. Once the holes are all drilled, it is vey important to remove all dust from the holes by using a vacuum or compressed air. After the holes are thoroughly cleaned you can then drop the epoxy capsules (provided) into the holes. Place the ½” stainless all-thread bolts into the holes and strike with a hammer to ensure that the capsule is broken and the epoxy is released. Allow the anchor bolts to “set” for about an hour to an hour and half, depending on the ambient temperature, or until secure. Once set you can then bolt down the unit. Using a grinder with a cut-off wheel, remove the excess all-thread protruding above finished grade. Open the gate and put the prop-rods (located in the pan) into place making sure to use the safety pin to prevent the gate from falling. Repeat the anchoring process using the holes located on the retention arm brackets. The all-thread bolts used on the inside of the pan must be ground off flush with the top of the nuts to ensure proper closing of the gate. Return the gate to the closed position.

## Slide 33
Attach lifting cable with stainless shackles

## Slide 35
Retention Arms

## Slide 36
Prop-rod

## Slide 37
Rotate prop-rod upward

## Slide 38
Slide prop-rod into position

## Slide 39
Place prop-rod end into the receiver

## Slide 40
Install safety pin

## Slide 41
Lower Retention Arm Bracket

## Slide 43
Using a rotor hammer and ½” masonry bit (provided) drill into the existing structure far enough to receive the wedge anchors and bolts (provided) by placing the bit into the pre-drilled holes in the wiper walls. Place the wedge anchors and bolts into the holes and tighten while ensuring the wiper walls are plumb and square to the gate surface. Sand the area around the bolt heads to remove the paint. Apply the two part putty (provided) to the sanded areas using the applicator provided. Allow the putty to harden and sand smooth.
STEP 14
Anchor the wiper walls to the existing structure.

## Slide 48
STEP 15
Protect the entire gate unit using duct tape and plastic to keep any concrete from getting on the gate unit.

## Slide 49
STEP 16
Place the second lift of concrete to finished grade. NOTE: It is critical to pour the concrete from the front side or “wet side” and vibrate to the back to avoid any air pockets.

## Slide 52
Wet Side
Dry Side

## Slide 54
Vibrating Concrete from “Wet Side” to “Dry Side”

## Slide 56
STEP 17
Using non-shrink grout, grout the area between the wiper walls and existing structure.
Wiper wall condition before grout

## Slide 57
Wiper Wall condition after grout

## Slide 58
STEP 18
Remove the tape and plastic, open the gate and put the prop-rods into place. Using a grinder with a cut-off wheel, cut the 4” drain off flush with the gate pan. Do not install a strainer. Re-paint the puttied areas of the wiper walls using the paint and roller provided.

## Slide 60: ESTIMATED INSTALLATION TIME
A typical retrofit installation, as we have illustrated here, under normal conditions usually takes four (4) men, three (3) days. The actual placement of the gate unit, i.e. leveling, anchoring, and placement of the second lift normally takes four (4) men, one and one half (1 ½) days.
For assistance please contact FloodBreak technical services.
FloodBreak, L.L.C.
2800 Post Oak, Blvd. Suite 5850
Houston, Texas 77056
(713) 980-6610
info@floodbreak.com